## Net Zero - Comm
Town of Ithaca NY Commercial: Base Code and Net-Zero Appendix Energy Requirements
Base Code Requirement | [6 empty] | Net-Zero Appendix Energy Requirements
Applicable buildings are required to provide 0.75 Watts/SF onsite solar unless they meet one of the 4 exceptions below. Area is based on the lesser of the Total Conditioned Area and the sum of the three largest floors' conditioned area (FLRA). If you meet one of the exceptions, then you must provide Off Site Renewable Energy according to Equation 4-11 below. | [6 empty] | Prescriptive Method, using the table provided; an energy model of building may require less Renewable Energy. Minimum Renewable Energy Requirement RE on-site + RE off-site >= RE min
Color Key | [6 empty] | Color Key
| Cells that require input from developer | [6 empty] | Cells that require input from developer
| Indicate outputs | [6 empty] | Indicate outputs
Section C405.15.1 | [6 empty] | Appendix CC Table CC103.1 |  | Area (SF) | kWh/SF/yr | kWh/yr Needed
Building Total Conditioned Area | [5 empty] | SF | Your Building Area Type |  |  |  | 0 |  | Indicate outputs
Sum of three largest floors' Conditioned Area | [5 empty] | SF | Your Building Area Type |  | 0 |  | 0
Lesser of the two (FLRA) |  |  |  |  | 0 | SF | RE min - Total Usage to Offset |  |  |  | 0 | kWh/yr
On Site Solar | [6 empty] | On Site Solar required
DC Watts |  |  |  |  | 0.75 | W/SF | REon-site (Base Code) |  |  |  | 0 | kWh/yr
Gross conditioned floor area of three largest floors |  |  |  |  | 0 | SF | Remaining kWh to offset annually |  |  |  | 0 | kWh/yr
Required on site solar PV capacity (W) |  |  |  |  | 0 | Watts | Commonly used local output factor, use solar calculator like PVWATTS (see below) |  |  |  |  | kWh/W
Required on site solar PV capacity (kW) |  |  |  |  | 0 | kW
Off Site Solar
Estimated Solar Output | [6 empty] | Estimated off-site solar wattage for net Zero |  |  |  | #DIV/0! | kW
Commonly used local output factor, use solar calculator like PVWATTS (see below) |  |  |  |  | 1.1 | kWh/W | Estimated annual solar output to be procured |  |  |  | 0 | MWh
Estimated annual solar output |  |  |  |  | 0 | kWh/year
TREoff |  |  |  |  | 0 | kWh | Equivalent RECs (1 REC = 1 MWh) |  |  |  | 0 | REC
PVWATTS Calculator
Exceptions: The following buildings or building sites shall comply with Section C405.15.2: 1. A building site located where an unshaded flat plate collector oriented toward the equator and tilted at an angle from horizontal equal to the latitude receives an annual daily average incident solar radiation less than 1.1 kBtu/ft2 per day (3.5 kWh/m2/day). 2. A building where more than 80 percent of the roof area is covered by any combination of permanent obstructions such as, but not limited to, mechanical equipment, vegetated space, access pathways or occupied roof terrace. Any building where more than 50 percent of the roof area is shaded from direct-beam sunlight by natural objects or by structures that are not part of the building for more than 2,500 annual hours between 8:00 a.m. and 4:00 p.m. 3. A building with gross conditioned floor area less than 5,000 square feet (465 m2). 4. A building with gross conditioned floor area less than 5,000 square feet (465 m2). | [6 empty] | Acronym definitions: RE - Renewable Energy FLRA - Sum of the 3 largest floors REC - Renewable Energy Certificate PV - Photovoltaic Solar Array DC - Direct Current kWh - kilowatt hours MWh - MegaWatt hours W - Watts SF - Square Feet
Equation 4-11 TREoff = Total off-site renewable energy in kilowatt-hours (kWh) to be procured. RENoff = Annual off-site renewable energy of 1.35 kilowatt-hours per watt of array capacity. FLRA = Sum of the gross conditioned area of all floors not to exceeed the combined floor area of the three largest floors. IREon = Annual on-site renewable energy generation of a new on-site renewable system, to be installed as part of the building project, whose rated capacity is less than the rated capacity required in Section C405.15.1. Note: The factor of 15 applies to the 15 year requirement for contract length. If there is no onsite solar, then the total amount of energy to be procured is: 1.35 kwh/watt * 0.75W/SF*FLRA * 15
Exceptions: The following buildings or building sites shall comply with Section C405.15.2:
Procurement Factor
| If 7.5 W/SF of on-site solar | 1 | PF |  |  |  | 1. A building site located where an unshaded flat plate collector oriented toward the equator and tilted at an angle from horizontal equal to the latitude receives an annual daily average incident solar radiation less than 1.1 kBtu/ft2 per day (3.5 kWh/m2/day).
| If less than 7.5 W/SF of on-site solar | 0.75 | PF |  |  |  | 2. A building where more than 80 percent of the roof area is covered by any combination of permanent obstructions such as, but not limited to, mechanical equipment, vegetated space, access pathways or occupied roof terrace.
| For unbundled RECs | 0.2 | PF |  |  |  | 3. Any building where more than 50 percent of the roof area is shaded from direct-beam sunlight by natural objects or by structures that are not part of the building for more than 2,500 annual hours between 8:00 a.m. and 4:00 p.m.
4. A building with gross conditioned floor area less than 5,000 square feet (465 m2).
| Assume less than 0.75 W/SF on-site… |  |  | If the full 0.75W/SF is on-site, then the
| Procurement Factor | 0.75 | PF | Procurement Factor (PF) is 1.0 |  |  | [NY] C405.15.2 Off-Site Renewable Energy
| Required RECs | #REF! | REC | Minimum purchase of NYSERDA Tier 1 REC
is officially 1,000 (tho perhaps as low as 500)
| Cost per REC | 24 | per REC | Current (10-8-25) cost of NYSERDA Tier 1 REC
| Total annual cost | #REF! | per year
#REF!
|  | #REF! | per apt per month
Note on K13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add two more rows with the same text
Note on H14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Have this formula determine the lesser of the two.